## UST Plan Check
UST PLAN CHECK
2025-01-09
|  | PLAN CHECK TYPE | UST Installation
FACILITY NAME
FACILITY ADDRESS
|  | AUTHORITY NUMBER | [5 empty] | FA NUMBER
SCOPE OF WORK, SUMMARY
Page No. |  | GENERAL APPLICATION
Service Request Updated
Correct Fee Paid
Contractor Information Complete on Application
Contractor Signed Application
Owner Information Complete
Equipment List Completed
Scope of Work Completed
Application signed by Owner or Owner Signature Authority Form submitted
Three sets of Plans submitted
All subcontractors identified
CERTIFICATION
|  |  | CSLB License is appropriate | [8 empty] | Exp:
C61-D40 is valid only for calibration work if issued after January 18, 2001
CSLB License Number:
Hazardous Substance Removal Certification (required
|  |  | for installation and removal) | [6 empty] | Exp:
|  |  | Active Worker's Compensation | [6 empty] | Exp:
The following MUST be conducted by a Qualified Installer: Installation of an underground storage tank and/or connected piping and completion of all work on the tank/piping manufacturer's installation checklist.
Qualified Installers must possess or work under the direct and personal supervision of an individual physically present at the work site who possesses all of the following: A valid, current contractor's license issued by the Contractor's State License Board, a valid, current certificate of training from the manufacturer(s) of the component(s) being installed and a valid and current ICC UST Installation/Retrofitting certificate.
ICC UST Installer/Retrofitter Certification Submitted
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
The following MUST be conducted by a Qualified Service Technician: All work related to UST leak detection monitoring equipment, (installation, repair, replacement, maintenance and calibration), Annual Monitoring Certification, Secondary Containment Testing (including initial testing of newly installed secondary containment systems).
Qualified Service Technicians must possess or work under the direct and personal supervision of an individual physically present at the work site who possesses all of the following: CSLB license as defined by 23 CCR 2715 (i)(1) or a Tank Tester's license issued to the individual by SWRCB, valid UST ICC Service Technician certificate, valid and current certificate of training from the manufacturer(s) of the component(s) being tested, repaired, or serviced. In the event that no training or certification exists, the local agency may approve comparable alternate training or certification.
ICC Service Technician Certification Submitted
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  | Contractor License is appropriate | [8 empty] | Exp:
C61-D40 is valid only for calibration work if issued after January 18, 2001
CSLB License Number:
Monitoring Equipment Manufacturer Certification Submitted
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Tank Manufacturer Training Certification Submitted
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Pipe Manufacturer Training Certification Submitted
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Under Dispenser Containment Manufacturer Training Certification Submitted
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Containment Sump Manufacturer Training Certification Submitted
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Transition Sump (vent, etc.) Manufacturer Training Certification Submitted
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Spill Containment Manufacturer Training Certification Submitted
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Other UST Component Manufacturer Training Certification Submitted
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Manufacturer:
|  |  |  | Exp: |  |  | Name:
|  |  |  | Exp: |  |  | Name:
Name(s) of Qualified Individual(s) with all required certifications:
ELD Company Information Submitted
Program for ELD Submitted
Soil Sampling Protocol and Lab Information Submitted
Name of Lab:
Certified Lab?
Page No. |  | OVERHEAD OF PLANS/DRAWINGS
Overhead View of Site--Must be submitted for all applications. Drawn to scale and include all the following that apply:
|  | Status | [6 empty] | Notes/Comments
North arrow
Scale of drawing
Building(s), neighboring buildings, streets and property lines--where applicable
Dispenser island(s)
Guard posts/bollards
|  |  |  | Tank | Size |  | Tank |  | Size |  |  | Tank |  | Size
|  |  | #1 |  |  | #3 |  |  |  |  | #5
|  |  | #2 |  |  | #4 |  |  |  |  | #6
Indicate Slope on Piping Toward Tank (inches per foot and direction)
Location of Monitoring Panel
Location of Overfill Alarm
Location of Emergency Shut Off(s)
Location of any Proposed or Existing Well(s) (observation, monitor, etc.)
PARTS LIST
|  | Status | [6 empty] | Notes/Comments
Parts list to be included on the drawings (must include make and model number and correspond to side view and/or end view drawings by number or letter).
PIPING
|  | Status | [6 empty] | Notes/Comments
Location of Product Piping and Termination of Pipe
Location of Vapor Recovery Piping and Termination of Pipe
Location of Vent Piping and Termination of Pipe
Location of Chase Piping
Vent Termination (must be 5 feet from any building or buildable property line)
Method(s) and location(s) of monitoring for piping
Type of piping labeled (i.e.: rigid FRP, Enviroflex, etc.)
Piping trench show the distances between pipes to bottom, sides and surface of trench.
Backfill material and type/thickness of cap over trench
Crossover Detail
End View of Piping
Piping is UL listed
Piping monitoring application is approved
Monitoring Equipment approved for application
Page No. |  | SIDE/TOP VIEW OF TANK AND EXCAVATION
|  | Status | [6 empty] | Notes/Comments
Tank Manufacturer identified
Size of tank(s) in gallons on plans
Dimensions of excavation and tank(s)
Distance from ends and sides of tank(s) to sidewalls of excavation
Depth of backfill beneath tanks and type of backfill material
Type and thickness of cap above tank(s)
Location of sumps and/or bungs
Location of spill containment and lids
Risers
ATG(s) (tank level probe)
Turbine(s)
Compartments in Tank
Drop Tube
Overfill prevention device(s)
Any slab or deadman with location and type of the tie down straps
Level or slope of tank
Hold down calculations for UST if water present in area (calculations can be listed on a separate letter)
Adapters
Sump lids and clamps (or other method of securing to lid)
Sealant between sump and manway skirt (if used)
Fill riser caps
VR Phase I riser caps
Location of Interstitial sensor, reservoir, riser, riser cap and, where applicable, at grade access box
Tank(s) is/are UL listed
Monitoring Equipment approved for application
SIDE/TOP VIEW OF SUMPS
|  | Status | [6 empty] | Notes/Comments
Method of attachment of sump to tank
Termination of sump secondary wall
Penetrations in sumps (boots, flanges, fittings-depict type)
Piping as it goes through penetrations
Penetrations are approved for use with proposed piping
Termination of secondary walls of pipe
Location of test boots
All piping and connections inside sump
Location and type of liquid sensor
Location and type of interstitial sensor
Hydrostatic Double Wall Monitoring: Type of liquid in interstice and directions for labeling
Communication testing apparatus location and type identified (ball valve, manometer, etc.)
Monitoring sensors are correct for application
Line Leak Detector
Line Leak Detector approved for application
Location of spill containment
All other equipment inside sump
Lids to manways
Type and depth of fill material and cap
Sump(s) are UL listed
Monitoring Equipment approved for application
Installation--Include a blowup drawing of the following:
|  | Status | [6 empty] | Notes/Comments
Manway Lid
Manway Skirt
Sump
Sump Lid
Spill Containment
Spill Containment meets requirements
Sump Top Hat
Interface between the manway skirt and sump top hat
Interface or connection between spill buckets
SIDE/TOP VIEW OF UNDER DISPENSER CONTAINMENT (UDC)
|  | Status | [6 empty] | Notes/Comments
Type of UDC (FRP, Shallow, Deep, etc)
Termination of UDC secondary wall (if a double wall UDC)
Penetration into UDC (depict type of penetration fitting)
All piping and conduits as they go through penetrations
Termination of secondary walls of pipe inside the UDC
Attachment of pipes, etc. to UDC infrastructure
Location of UDC liquid sensor
Location of UDC interstitial sensor
Hydrostatic Double Wall Monitoring: Type of liquid in interstice and directions for labeling
Communication testing apparatus location and type identified (ball valve, manometer, etc.)
Flex connectors
Shear valves
Adequate labeling of components in plans
UDC is UL listed
Monitoring sensors are approved for application
SIDE/TOP VIEW OF PIPE TRANSITIONS AND PENETRATIONS
|  | Status | [6 empty] | Notes/Comments
Penetrations of underground piping into basement or to ground surface--include the pipe or collar that provides a conduit for the double wall pipe.
SIDE/TOP VIEW OF VENT RISER/SUMP
|  | Status | [6 empty] | Notes/Comments
Tank vent termination is a minimum of 12 feet above grade
Depict the flex connectors and secondary boots
Location of Vent Sump annular sensor
Location of Vent Sump liquid sensor
Hydrostatic Double Wall Monitoring: Type of liquid in interstice and directions for labeling
Communication testing apparatus location and type identified (ball valve, manometer, etc.)
Transition from flexible or fiberglass piping to above ground piping-include protection from sunlight and elements, as well as construction of aboveground piping.
Vent Sump UL listed
Monitoring sensors are approved for application
SIDE VIEW OF GUARD POSTS/BOLLARDS
|  | Status | [6 empty] | Notes/Comments
Bollards or guard posts to include: construction, diameter, height, distance between posts, distance from dispensers, depth and diameter of footing.
VPH LAYOUT
|  | Status | [6 empty] | Notes/Comments
New installations: Drawing and/or table of proposed monitored zones (vacuum, pressure, hydrostatic). Include vacuum volume for each vacuum monitored zone.
UST REMOVAL
|  | Status | [6 empty] | Notes/Comments
Removal Application

## Equipment and Monitoring
UST Plan Check Equipment and Monitoring Plan
Overfill Options:
Alert the transfer operator when the tank is 90 percent full by restricting the flow into the tank or triggering an audible and visual alarm; or
Restrict delivery of flow to the tank at least 30 minutes before the tank overfills, provided the restriction occurs when the tank is filled to no more than 95 percent of capacity; and activate an audible alarm at least five minutes before the tank overfills; or
Provide positive shut off of flow to the tank when the tank is filled to no more than 95 percent of capacity; or,
| Tank(s) | [7 empty] | Provide positive shut off of flow to the tank so that none of the fittings located on the top of the tank are exposed to product due to overfilling.
|  | Product | Size | System Type | Manufacturer | Part No. | Approved for Use
Tank 1:
Tank 2:
Tank 3:
Tank 4:
Tank 5:
Tank 6:
Tank Monitoring Method
Monitoring Method the same for all tanks?
Piping and Sump(s)
| Piping Information |  | Size |  | Manufacturer | Part No. | Approved for Use
Product Piping
Vapor Return Piping
Vent Piping
Chase Piping
add
add
Piping Monitoring Method
Monitoring Method the same for all piping?
| Sump Information |  |  | Manufacturer |  | Part No. | Approved for Use
Turbine
Flex Connector
Line Leak Detector
Penetration Fitting
Penetration Fitting
Piping Sump
Fill Sump
Vent Transition Sump
Transition Sump
add
add
Interstitial Monitoring of Sump
Piping in Sump Monitoring Method
Monitoring Method the same for all sumps?
Under Dispenser Containment(s)
| Under Dispenser Containment (UDC) Information |  |  | Manufacturer |  | Part No. | Approved for Use
Shear Valves
UDC
UDC Interstitial Monitoring Method
Piping Monitoring Method in UDC
Monitoring Method the same for all under dispenser containment?
Overfill/Spill Containment
| Overfill/Spill Containment Information |  |  | Manufacturer |  | Part No. | Approved for Use
Drop Tube
Overfill Method
| Spill Containment & Lids | [6 empty] | Use:
In Tank Probe
Insert Diagrams or Layout Drawings Here

## Inspection Worksheet
Environmental
Management
Department
Val F. Siebal, Director
UST INSPECTION WORKSHEET
Facility Name
Facility Address
ECD Authority Number | [7 empty] | FA Number
Project Summary
Tank Set
|  |  | Tank #1 |  | Tank #2 |  | Tank #3 |  | Tank #4 |  | Tank #5 | Tank #6 |  | Title 23, 2635 (a)(1)(3)
Date | [13 empty] | Before installation, the tank shall be tested for tightness at the installation site in accordance with the manufacturer's written guidelines. If there are no guidelines, the primary and secondary containment shall be tested for tightness with air pressure at not less than 3 pounds per square inch. In lieu of the above, an equivalent differential pressure test, expressued in inched of mercury vacuum, in the intersitial space of the secondary containment is acceptable. The pressure (or vacuum in the intersitial space) shall be maintained for a miniumum of 30 minutes to determine if the tank is tight. If the tank fails the tightness test, as evidenced by soap bubbles, or water droplets, installation shall be suspended unti the tank is replaced or repaired by a factory authorized repair service. Following repair or replacement, the tank shall pass a tightness test.
| Tank Manufacturer |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A | N/A
| Monitoring Method |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A | N/A
| Monitoring Equipment |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A | N/A
Contents |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A | N/A
Size in Gallons |  |  | N/A |  | N/A |  | N/A |  | N/A |  | N/A | N/A
Pre-Install Test |  |  | Tanks shall be installed per manufacturer's installation instructions and guidelines.
Test Type
Initial Reading
Final Reading
Result
Comments/Notes:
Primary Piping | [7 empty] | Test | 50-100 psi for one hour | [12 empty] | Enter test parameters and length of time per manufacturer's testing requirements
Follow manufacturer's installation testing requirements
Additional product primary piping and retests
Product Primary Piping |  |  | N/A | N/A | N/A | N/A | N/A | N/A | [5 empty] | CCR Ti 23 2636: Design, Construction, Intsallation, Testing, and Monitoring Requirements for Piping
| Date | [12 empty] | All new primary piping and secondary containment systems shall be tested for tightness after installation in accordance with manufacturer's guidelines. Primary pressurized piping shall be tested for tightness hydrostatically at 150 percent of design operating pressure or pneumatically at 110 percent of design operating pressure. If the calculated test pressure for pressurized piping is less than 40 psi, 40 psi shall be used as the test pressure. The pressure shall be maintained for a minimum of 30 minutes and all joints shall be soap tested. A failed test, as evidenced by the presence of bubbles, shall require appropriate repairs and retesting. If there are no manufacturer's guidelines, secondary containment systems shall be tested using an applicable method specified in an industry code or engineering standard. Suction piping and gravity flow piing which cannot be isolated from the tank shall be tested after installation in conjunction with an overfilled volumetric tank integrity test or other test method meeting the requirements of section 2643(f), if approved by the local agency.
Beginnning Reading
End Reading
Result
Additional vent primary piping and retests
Vent Primary Piping |  |  | N/A | N/A | N/A | N/A | N/A | N/A
Date
Beginnning Reading
End Reading
|  | Result | [10 empty] | Fail | Fail | Fail | Fail | Fail | Fail | Fail | Fail | Fail
Additional vapor return primary piping and retests
Vapor Return Primary Piping |  |  | N/A | N/A | N/A | N/A | N/A | N/A
Date
Beginnning Reading
End Reading
|  | Result | [10 empty] | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass | Pass
Secondary Piping | [7 empty] | Test | 5-10 psi for one hour
Follow manufacturer's installation testing requirements
Additional product secondary piping and retests
Product Secondary Piping |  |  | N/A | N/A | N/A | N/A | N/A | N/A
Date
Beginnning Reading
End Reading
Result
Additional vent secondary piping and retests
Vent Secondary Piping |  |  | N/A | N/A | N/A | N/A | N/A | N/A
Date
Beginnning Reading
End Reading
Result
Additional vapor return secondary piping and retests
Vapor Return Secondary Piping |  |  | N/A | N/A | N/A | N/A | N/A | N/A
Date
Beginnning Reading
End Reading
Result
Sumps, Turbine and Fill | [7 empty] | Test | 5-10 psi for one hour
Follow manufacturer's installation testing requirements
Additional sumps and retesting
Tubine Sump |  |  | N/A | N/A | N/A | N/A | N/A | N/A
Date
Beginnning Reading
End Reading
Result
Fill Sump |  |  | N/A | N/A | N/A | N/A | N/A | N/A
Date
Beginnning Reading
End Reading
|  | Result | [10 empty] | Fail | Fail | Fail | Fail | Fail | Fail | Fail | Fail | Fail
Transition, Vent Sump(s) | [8 empty] | Test: | 5-10 psi for one hour
Manufacturer's installation testing requirements
|  |  | Vent |  | Transition
Date
Beginning Reading
End Reading
Result
Under Dispenser Containment | [8 empty] | Test | 5-10 psi for one hour
Follow manufacturer's installation testing requirements
Underdispenser Containment (UDC)
Date
Beginnning Reading
End Reading
|  | Result | [10 empty] | Fail | Fail | Fail | Fail | Fail | Fail | Fail | Fail | Fail

## Inspection Report
Environmental
Management
Department
Val F. Siebal, Director
UST INSPECTION REPORT
Facility Name
Facility Address
ECD Authority Number | [7 empty] | FA Number
Project Summary
Tank Set
|  |  | Tank #1 |  | Tank #2 |  | Tank #3 |  | Tank #4 |  | Tank #5 |  | Tank #6
Date
Contents
Size in Gallons
Result
Comments/Notes:
Primary Piping Install/Repair Testing | [7 empty] | Test | 50-100 psi for one hour
Follow manufacturer's installation testing requirements
Additional product primary piping and retests
Product Primary Piping
Date
Result
Additional vent primary piping and retests
Vent Primary Piping
Date
Result
Additional vapor return primary piping and retests
Vapor Return Primary Piping
Date
Result
Secondary Piping Installation/Repair Testing | [7 empty] | Test | 5-10 psi for one hour
Follow manufacturer's installation testing requirements
Additional product secondary piping and retests
Product Secondary Piping
Date
Result
Additional vent secondary piping and retests
Vent Secondary Piping
Date
Result
Additional vapor return secondary piping and retests
Vapor Return Secondary Piping
Date
Result
Tank Top Sump | [7 empty] | Test | 5-10 psi for one hour
Follow manufacturer's installation testing requirements
Additional sumps and retesting
Tubine Sump
Date
Result
Final Communication Test
Result
Fill Sump
Date
Result
Final Communication Test
Result
|  |  | Vent |  | Transition |  | Transition
Date
Result
Final Communication Test
Result
Under Dispenser Containment | [8 empty] | Test | 5-10 psi for one hour
Follow manufacturer's installation testing requirements
Underdispenser Containment (UDC) |  |  | 1/2 | 3/4 | 5/6 | 7/8 | 9/10 | 11/12 | 13/14 | 15/16 | 17/18 | 19/20 | 21/22 | 23/24
Date
Result
Final Communication Test
Result
Misc.
Hydrostatic Fluid labeled |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Vacuum Hoses Long Enough to Allow Sensors to Surface |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Proper filling of hydrostatically monitored annular space(s) (per manufacturer's instructions) |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Hydrostatic Testing Port(s) Accessible |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Vacuum Testing Port(s) Accessible |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Positive Shutdown Verified |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Failsafe Verified |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Shear Valve(s) Installed |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Shear Valve Bracket(s) Tight |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Overfill Installed |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Emergency Shutoff(s) |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
ISD Installed |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Monitoring Well(s) |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Healy Clean Air Separator/OPW Vaporsaver |  |  | 7/8: q Yes; 9/10: q No; 11/12: q N/A
Comments/Notes:
Final Monitoring System Testing
|  |  | Date: |  |  |  | Specialist:
Tank
Monitoring Method
Annular Sensor, Part Number
Result
Piping (VPH)
Monitoring Method
Product Piping Interstital Sensor, part number
Result
Vapor Return Piping Intersitial Sensor, part number
Result
Vent Piping Interstitial Sensor, part number
Result
Sump Containment and Piping
Inerstitial Monitoring Method
Sump Interstitial Sensor Manufacturer and Part Number
Piping Sump Sensor, Part Number
Piping Sump Intersitital Sensor
Piping Sump Liquid Sensor
Fill Sump Interstitial Sensor
Fill Sump Liquid Sensor
Vent Sump Interstitial Sensor
Vent Sump Liquid Sensor
Transitition Sump Interstital Sensor
Transition Sump Liquid Sensor
Under Dispenser Containment
Intersitital Monitoring Method
UDC Interstitial Sensor, Part Number
Result
UDC Liquid Sensor, Part Number
Result
Vacuum Monitored Zone Table
Verify the secondary containment volumes per zone for vacuum monitoring from the submitted information. Determine the secondary containment factor from a current chart of volumes per manufacturer. Add multiple containment volumes if more than one component is included in the zone. If piping, multiply the appropriate factor by the length of piping. If there are multiple piping runs, add all to determine the total containment volume.
Final Communciation Test
Programmed Sensor Number |  | Description | 7/8: Total Secondary Containment Volume Programmed; 11/12: Secondary Containment Volume Verified; Follow manufacturer's installation testing requirements 15/16: No vacuum; Follow manufacturer's installation testing requirements 17/18: High Liquid; Follow manufacturer's installation testing requirements 19/20: Communciation Test; Follow manufacturer's installation testing requirements 21/22: Location
S1
S2
S3
S4
S5
S6
S7
S8
S9
S10
S11
S12
S13
S14
S15
S16

## UST Construction Summary
Environmental
Management
Department
Val F. Siebal, Director
UST CONSTRUCTION SUMMARY
Facility Name
Facility Address
ECD Authority Number |  |  | FA Number
Project Summary
Required Testing/Inspection |  | Date Completed |  | Comments
Required Testing per Permit Application
Tank Primary
Tank Secondary
Primary Piping
Secondary Piping
Sump Integrity
Vent Integrity
Transition Integrity
Under Dispenser Integrity
Intersitial Fill (per manufacturer's instructions)
Overfill Containment
Tank Tightness
Piping Tightness
Secondary Containment, after backfill
Required Testing Report |  | Date Completed |  | Comments
Enhanced Leak Detection (before initial delivery)
Final Monitoring System Certification
Detailed As-Built drawing including vacuum, pressure or hydrostically monitored zones.
California Environmental Reporting System |  | Date Completed |  | Comments
CERS Completed and Approved
UST
UST Certification of Installation/Modification
HMP
Sacramento County Environmental Compliance Department |  | Date Completed |  | Comments
Inspection Notes/ Diagram Completed
Classification Form
HAPP
Service Request Updated
No Further Action Letter
6 Month Secondary Containment Testing
Operating Permit Issuance
Plans/Permit Submitted for Imaging
Completion of Final Inspection Letter

## UST Removal Summary
Environmental
Management
Department
Val F. Siebal, Director
UST REMOVAL SUMMARY
Facility Name
Facility Address | [5 empty] | T
ECD Authority Number |  |  |  | FA Number
Project Summary
Required per Permit Application |  |  | Date Completed |  | Comments
Tank(s) Removed
Tank(s) Cleaned
Rinsate Manifest
Tank Destruction Certificate
Hazardous Waste Tank Closure Certification
Sampling Under Tank (s)
samples per tank
Additional Sampling
Sampling Under Dispenser
Sampling Under Piping
Chain of Custody
Map of Sampling Location(s)
Sampling Conclusion Form
California Environmental Reporting System |  |  | Date Completed |  | Comments
CERS Completed and Approved
UST Submittal for Permanently Closed Tanks
HMP
Sacramento County Environmental Compliance Department |  |  | Date Completed |  | Comments
HAPP - Status of Tank 02
HAPP - Update PE Code(s) Status
Service Request Updated
No Further Action Letter
Plans/Permit Submitted for Imaging

## Drop Down Menu
UST Plan Check Tab | Equipment and Monitoring Tab | Inspection Worksheet Tab | Inspection Report Tab | Summary Tab
UST Installation
UST Removal | Vacuum
Permanent Closure In Place (PCIP) | Pressure | Pass | Pass
UST Upgrade Including Piping | Hydrostatic | Fail | Fail
UST Upgrade Without Piping | Dry | N/A | N/A
UST Repair (storage tank, piping or monitoring system) | N/A |  | Yes | Yes
UST Repair or Replacement of Spill Container | Yes |  | No | No
N/A | No |  | N/A | Incomplete
Yes | N/A |  |  | N/A
No | Straight
Incomplete | Flapper
A, General Engineering | Alarm
C-10, Electrical | Alarm and Flapper
C-34 Pipeline | Electronic
C-36 Plumbing | Mechanical
C-61(D-40) | Inventory Only
Hazardous Substances Removal | Tank Monitoring
SWRCB Tank Tester License | Overfill
Same as Previous
Pressure
Suction
Gravity